## Rectangle
Rectangular Tank
* * * ALL ORANGE CELLS MUST BE FILLED * * * |  |  |  | Depth of Lid not Submerged |  |  | 0.5
Values for f, Ka, and e can be found in Tables 1, 2, and 3 in the accompanying document. |  |  |  | Depth of Lip not Submerged |  |  | 0
|  |  |  | Depth of Thicker Base not Submerged |  |  | 0
Disclaimer: Use of this calculator does not guarantee the proper function or performance of any product manufactured in accordance with the data herein. It is the user's responsibility to ensure their product is designed and manufactured to resist all forces applied.
Basic Dimensions
Lid Thickness (L) | 0.5 | (feet)
Lid Hole Diameter (H1) | 12 | (inches)
Lid Hole Diameter (H2) - If tank has only one hole, leave blank. | 0 | (inches)
Lid Hole Diameter (H3) - If tank has only one hole, leave blank. | 0 | (inches)
Length of Tank (A) | 5 | (feet)
Width of Tank (B) | 3 | (feet)
Height of Tank Excluding Lid (C) - This value includes the base thickness but excludes the lid thickness. | 3.5 | (feet)
Depth of Bury (Y) - This measurement extends from the ground level to the top of the lid. | 2 | (feet)
Wall Thickness (T) | 0.5 | (feet)
Base Thickness (E) | 0.5 | (feet)
Distance to Groundwater (GW) | 4 | (feet)
Customizations To Add Ballast
Add Concrete Inside the Tank:
Initial Inside Height of Tank - This measurement is the value of C - E. | 3 | (feet)
Add concrete inside the tank to make thicker base? | 0 | (feet)
If yes, how much? (U) If no, enter a value of 0. Please note: The value entered must be less than the inside height of the tank.
Increase Thickness of the Base:
Initial Base Thickness - This measurement is the value of E. | 0.5 | (feet)
Add concrete below the base of the tank to make thicker base? | 0 | (feet)
If yes, how much? (F) If no, enter a value of 0.
Create Lip:
Extend the base horizontally to create a lip? - The lip will be the thickness of E plus F, below, and it will extend this horizontal distance, P, from all four tank walls. | 0 | (feet)
If yes, how much? (P) If no, enter a value of 0.
Summary of Final Measurements after Ballast Customizations
Final Base Thickness - This measurement is the sum of E and F. | 0.5 | (feet)
Lip Thickness - This measurement is the sum of E and F. | 0.5 | (feet)
Total Height of the Tank from the Top of the Lid to the Bottom of the Base - This measurement is the sum of L, C, and F. This is equivalent to the sum of L, C - E, E, and F. | 4 | (feet)
Final Inside Height of Tank - This measurement is the value of C - E - U. | 3 | (feet)
Final Volume of Tank | 24 | (cf)
Final Volume of Tank | 179.5325 | (gallons)
Unit Weights
Unit Weight of Water | 62.4 | (lb/cf)
Unit Weight of Dry Soil | 110 | (lb/cf)
Unit Weight of Submerged Soil | 47.6 | (lb/cf) |  | Depth of tank NOT submerged |  |  | 2
Unit Weight of Saturated Soil | 120 | (lb/cf) |  | Surface Area of Lip |  |  | 0
Unit Weight of Concrete | 145 | (lb/cf) |  | Depth of tank that IS submerged |  |  | 2
|  |  |  | Height of Tank |  |  | 4
Changes in Total Concrete Weight Due to Customizations |  |  |  | Y+L+C+F-GW |  | 2
Weight of extra concrete inside tank used to create thicker base (Weight of extra concrete due to U) | 0 | (lb) |  | L+C+F-DOTNS |  | 4 |  | 0
Weight of extra concrete on bottom of tank used to create thicker base (Weight of extra concrete due to F) | 0 | (lb)
Weight of extra concrete due to lip (Weight of extra concrete due to P) | 0 | (lb) |  | C+Y+L+F-GW |  | 2 | (feet)
Weight of concrete removed due to lid hole | 56.9414 | (lb) |  | C+Y+L+F |  | 6 | (feet)
Soil and Concrete Weights |  |  |  | Perimeter |  | 16 | (feet) | 30
Weight of Soil on Lid | 3300 | (lb) |  | Pdry |  | 290.4 | (lb/ft)
Weight of Soil on Lip | 0 | (lb) |  | Psat |  | 33.6 | (lb/ft)
Weight of Lid Alone | 1030.5586 | (lb) |  | P |  | 987.864 | (lb/ft)
Weight of Empty Tank - This value is the sum of weights of the body of the tank, the tank lid, the lip (P, if applicable), the thickened base (F, if applicable), and the extra concrete inside tank (U, if applicable), minus the weight of the concrete removed due to the hole in the lid. | 5163.0586 | (lb) |  | Rsliding |  | 4741.7472 | (lb)
Water in Tank
Water Level in Tank - Please note: The value entered must be less than the final inside height of the tank. | 0 | (feet)
Weight of Water in Tank | 0 | (lb)
|  |  | SG |  | 2.75
Weight of System Components |  |  | Void Ratio |  | 0.85
Total Weight of Soil on Tank | 3300 | (lb) | Gamma Saturated |  | 121.427
Total Weight of Concrete | 5163.0586 | (lb)
Total Weight (Tank, Water in Tank, and Soil) | 8463.0586 | (lb)
Table 1
Sliding Resistance
Specific Gravity of Soil, SG | 2.75
Friction Factor (Found in Table 1), f | 0.3
Void Ratio (Found in Table 3), e | 0.85
Ratio of Lateral to Vertical Earth Pressure (Found in Table 2), Ka | 0.33 |  | P Dry: total soil force from the ground level to the water table
Sliding Resistance | 4741.7472 | (lb)
Uplift Force
Uplift Force | 1872 | (lb) | P Buoyant: total buoyant force of the earth against the wall below the water table
Safety Factor | 2
Uplift Force with Safety Factor | 3744 | (lb)
Additional Ballast Required | NONE | (lb)
| 3276 | << This is the uplift force value given by the old equation
| 1872 | << Given by the new equation written on Friday

## Round
Manhole
* * * ALL ORANGE CELLS MUST BE FILLED * * *
Values for f, Ka, and e can be found in Tables 1, 2, and 3 in the accompanying document.
Disclaimer: Use of this calculator does not guarantee the proper function or performance of any product manufactured in accordance with the data herein. It is the user's responsibility to ensure their product is designed and manufactured to resist all forces applied.
Basic Dimensions
Inside Diameter of Manhole (D) | 5 | (feet) | Volume of manhole walls | 43.1969
Lid Thickness (L) | 12 | (inches) | Area of inside of manhole | 19.635
Height of Manhole From Top of Base to Top of Lid - This value includes the height of the lid plus the barrel section, but excludes the height of the base. | 6 | (feet) | Area of outside manhole/lid | 28.2743
Height of Manhole Barrel Section From Top of Base to Bottom of Lid (C) - This value is the height of the barrel section. | 5 | (feet) | weight of lid | 3523.2471
Depth of Bury (Y) - This measurement extends from the ground level to the top of the lid. | 4 | (feet) | Area of outside of base | 28.2743
Wall Thickness (T) | 6 | (inches) | Volume of lid with hole removed | 24.2983
Base Thickness (E) | 12 | (inches) | Volume of manhole | 169.646
Lid Diameter - This value is the sum of D and 2*T. | 6 | (feet) | Volume of hole in lid | 3.9761
Lid Hole Diameter (H4) | 27 | (inches) | Volume of base | 28.2743
Distance to Groundwater (GW) | 9 | (feet) | weight of manhole walls | 6263.5504
Depth of Manhole Not Submerged in Water | 5 | (feet) | weight of base | 4099.7784
Customizations
Create Lip:
Extend the base horizontally to create a lip? | 0 | (inches)
If yes, how much? (P) If no, enter a value of 0.
Thickness of lip (E) - This measurement is determined by the value entered for the base thickness. The lip thickness is equal to that of the base. | 12 | (inches)
Add Penetrations:
Diameter of Penetration #1 (H1) - Enter a value of 0 if there is no Penetraion #1. | 0 | (inches)
Diameter of Penetration #2 (H2) - Enter a value of 0 if there is no Penetraion #2. | 0 | (inches)
Diameter of Penetration #3 (H3) - Enter a value of 0 if there is no Penetraion #3. | 0 | (inches)
Unit Weights
Unit Weight of Water | 62.4 | (lb/cf)
Unit Weight of Soil | 110 | (lb/cf)
Unit Weight of Submerged Soil | 47.6 | (lb/cf) |  | 0
Unit Weight of Concrete | 145 | (lb/cf)
Unit Weight of Saturated Soil | 120 | (lb/cf)
Changes in Total Concrete Weight Due to Customizations
Weight of extra concrete due to lip (Weight of extra concrete due to P) | 0 | (lb)
Total weight removed due to penetrations in barrel section | 0 | (lb)
Weight of concrete removed due to lid hole | 576.5313 | (lb)
Soil and Concrete Weights |  |  | Total Height | 22 | ft
Weight of Soil on Lid | 12440.7069 | (lb)
Weight of Soil on Lip | 0 | (lb) | P | 3801.336 | lb/ft
Weight of Lid Alone | 3523.2471 | (lb) | R sliding | 21496.0487
Weight of Manhole (Weight of Barrel Section, Lip, and Lid) | 13886.5758 | (lb)
Weight of System Components
Total Weight of Soil | 12440.7069 | (lb)
Total Weight of Concrete | 13886.5758 | (lb) | diameter of base | 6
Total Weight (Manhole and Soil) | 26327.2827 | (lb)
|  |  | circumference of base | 18.8496 | ft
Sliding Resistance
Specific Gravity of Soil | 2.75
Friction Factor (Found in Table 1), f | 0.3 |  | Total weight of manhole (includes the subtractions for 3 penetrations and the lid hole) | 13886.5758
Void Ratio (Found in Table 3), e | 0.85 |  | Weight of dry soil above manhole | 12440.7069
Ratio of Lateral to Vertical Earth Pressure (Found in Table 2), Ka | 0.33 |  | Weight of wet soil above manhole | 5383.4332
Sliding Resistance |  | (lb)
Uplift Force
Uplift Force | 3528.6369 | (lb) | Weight of dry soil above lip | 0
Safety Factor | 2 |  | Area of lip | 0
Uplift Force with Safety Factor | 7057.2737 | (lb)
5
|  |  | Weight Removed Due to Penetration #1 | 0
Additional Ballast Required | NONE | (lb) | Weight Removed Due to Penetration #2 | 0
|  |  | Weight Removed Due to Penetration #3 | 0
|  |  | Total Weight Removed Due to Penetrations | 0
|  |  | 5292.9553 |  | 14114.5475
|  |  | 5292.9553 |  | 5292.9553
|  |  | FALSE |  | 65707.7927
|  |  | 0 |  | 66473.7129

## Tables
To access Tables 1, 2 and 3, click HERE