## Slide 1: Hatches and Holes Design Impacts on Underground Structures
Precast Concrete Association of New York
Ronald Thornton, P.E.
Executive Director

## Slide 2: Learning Objectives
Review the general principles and ASTM standards involved in the design of round, square, and rectangular structures
Discuss ACI 318 and PCI provisions regarding openings in slab systems
Identify various types of access devices including hatches, grates, & manhole frames and how live loads applied to these devices are transferred to the slab
Review pipe-to-wall connections such as mortar, gasket, & flanged sleeves
Establish limitations and measures for replacing interrupted reinforcing steel
Location of wall openings relative to horizontal joints

## Slide 3: Holes and Hatches
Almost all underground structures require some type of opening

## Slide 4: Holes and Hatches
Corner-outs like this should be avoided

## Slide 5: Holes and Hatches
Openings need to be properly reinforced

## Slide 6: Holes and Hatches
Should openings cross a horizontal joint?
Openings can also affect lifting & rigging
We will discuss

## Slide 7: ASTM Standards for Precast Underground Structures
Materials & Manufacturing ASTM | Related Products | Loads | Design Standard
C478 | Round Manholes | N/A | ACI 318
C858 | Utility Structures | C857 | ACI 318
C913 | Water & Wastewater Structures | C890 | ACI 318
C1227 | Septic Tanks | C890* | ACI 318
C1613 | Grease Traps | C890 | ACI 318
*C1227 specifies lighter loads for residential tanks |  |  | 

## Slide 8: Other Design & Load Specifications
AASHTO LRFD – ASTM C1889
  HL93 Loading
Aircraft Loads – FAA Circular 5320-6G, Appendix B
Railroad Loading – AREMA (American Railway Engineering and Maintenance-of-Way Association)
    Cooper E80
ACI 350 – Environmental Engineering Structures
State DOT Specifications

## Slide 9: Design of Underground Vaults
Break down a structure to individual members
  Top Slab
  Walls
    Mono Top
    Risers
    Mono/Integral Base
  Base slab
TOP SLAB
BASE SLAB
WALLS

## Slide 10: Design of Underground Vaults
Two (2) Basic Load Types
  Concentrated
  Uniform or Superimposed
Uniform or Superimposed load, w(lbs/sf)
Concentrated Load
P (lbs)

## Slide 11: Design of Underground Vaults
Define Load Types and Categories
  ACI 318 Designations
    Dead Loads, D
    Live Loads, L
    Lateral Earth & Hydrostatic Loads, H
    Seismic, E
    Wind, W
    Snow, S

## Slide 12: Design of Underground Vaults
ACI 318 Load Combinations
  U = Ultimate Load
    1.4D
    1.2D + 1.6L + 0.5S
    0.9D + 1.0E
    1.6H

## Slide 13: Design of Underground Vaults
Top Slab Design
  Traffic Loads
  Non-Traffic (Pedestrian)
TOP SLAB

## Slide 14: Design of Underground Vaults
Traffic Loads
  H20
  HS20
  HS20-44
  HS20 Plus 30% Impact
THERE IS NO DIFFERENCE!!!

## Slide 15: Design of Underground Vaults
Vehicle Loads
  ASTM C857
  ASTM C890
Top slab designs are typically based on a single wheel load
Earth fill3 <2’ are considered concentrated
Earth fills >2’ are distributed through fill

## Slide 16: Design of Underground Vaults
Vehicle Loads
Grade
2’-0”
(A16 Load)

## Slide 17: Design of Underground Vaults
Walls
  Top Slab
  Walls
    Mono Top
    Risers
    Mono/Integral Base
  Base slab
JOINTS

## Slide 18: Design of Underground Vaults
Lateral Earth Loads
  Active earth pressure above and below water table
    Load increases with depth
  Live load surcharge
    Considered uniform for simplicity
Effective lateral soil pressure more than doubles below the water table depth

## Slide 19: Design of Underground Vaults
Base Slab
BASE SLAB

## Slide 20: Design of Underground Vaults
Base Slab
Add all Downward Forces
  Total Number of Wheels
  + Total Earth Fill
  + Self Weight of Structure
  - Base slab weight
Divide by area of base slab

## Slide 21: Reinforced Concrete Design
Concrete Thickness
  Sufficient to meet minimum reinforcement cover and withstand design loading conditions.
Reinforcement
  Reinforcement design by structural calculations as required by code or as proven by testing.

## Slide 22: Reinforced Concrete Design

## Slide 23: Reinforced Concrete Design

## Slide 24: Reinforced Concrete Design
Ultimate Forces
  = Σ Dead & Live Load Moment & Shear Forces x Applicable Load Factors

## Slide 25: Reinforced Concrete Design
Capacity or Nominal Moment
c
d
Bar Cover
t

## Slide 26: Reinforced Concrete Design
Bar Size | Diameter (in) | Ab (in2)
3 | 3/8” = .375 | .11
4 | ½” = .500 | .20
5 | 5/8” = .625 | .31
6 | ¾” =.750 | .44
7 | 7/8” =.875 | .60
8 | 1.00 | .79
9 | 1.128 | 1.00
10 | 1.270 | 1.27
11 | 1.410 | 1.56
Source: Concrete Reinforcing Steel Institute - CRSI
Slab
#5 @ 9”oc
Beam
(3) # 6 Bars

## Slide 27: Openings in Slab Systems
ACI 318-19
8.5.4 Openings in slab systems
8.5.4.1 Openings of any size shall be permitted in slab
systems if shown by analysis that all strength and serviceability
requirements, including the limits on deflections, are
satisfied.
  Total quantity of reinforcement in the slab shall be at least equal to that required for the slab without the opening

## Slide 28: Openings in Slab Systems
Provide additional reinforcing equal to bars interrupted by the opening, half each side and in the same plane
Use same number of bars interrupted or equivalent area-of-steel of interrupted bars:
  Example – (4) #4 bars interrupted = 4 * 0.20 = 0.80in2
  Alternate – (2) #6 replacement bars = 2 * 0.44 = 0.88in2
Provide #4 diagonal trim bars at openings for crack control

## Slide 29: Openings in Slab Systems

## Slide 30: Openings in Slab Systems

## Slide 31: Openings in Slab Systems

## Slide 32: Openings in Slab Systems

## Slide 33: Openings in Slab Systems

## Slide 34: Openings in Slab Systems

## Slide 35: Openings in Slab Systems

## Slide 36: Openings in Slab Systems
Design Beam in the Long Direction

## Slide 37: Trim Bars
ASTM C478/C478M
  13.4.3 A Layer of reinforcement shall have a minimum area of 0.12in2/linear ft [250mm2/linear m] in both directions.
  Openings in flat slab tops shall be additionally reinforced with a minimum of the equivalent of 0.20in2 [130mm2] of steel at 90°. Straight rods used to reinforce openings shall have a minimum length equal to the diameter of the opening plus 2in.

## Slide 38: Openings in Slab Systems
Trim bars are not the same as replacement steel

## Slide 39: Openings in Walls
Clear openings – Round or Rectangular
Gaskets
Sleeves
Knockouts
Corner Openings – Try to avoid
Slide Gates
    Retaining interior or exterior water?
Weirs

## Slide 40: Reinforced Concrete Design
Finite Element Analysis
  Accurately shows areas of maximum stress
  Time consuming method
  Not often justified

## Slide 41: Reinforced Concrete Design
Finite Element Analysis
  Accurately shows areas of maximum stress
  Time consuming method
  Not often justified

## Slide 42: Reinforced Concrete Design

## Slide 43: Openings in Slab Systems

## Slide 44: Openings in Slab Systems

## Slide 45: Openings in Slab Systems
THIN WALL
KNOCKOUT
(UNREINFORCED)

## Slide 46: Openings in Slab Systems
Round Manhole Walls

## Slide 47: Openings in Slab Systems
Round Manhole Walls

## Slide 48: Lifting & Handling
Factors to Consider
  Weight of the piece
  Center-of-gravity
  Member thickness
  Direction of lift (shear or tension)
  Hook height
  Fleet Angle
  Concrete Strength
  Adhesion to form

## Slide 49: Lifting & Handling
Local Stress
  Tension Loading
  Shear Loading

## Slide 50: Lifting & Handling
Global Stress
  Openings will reduce the section that resists bending stress
PCI Design Manual Figure 5.3.2.1

## Slide 51: Lifting & Handling
Global Stress
  Openings will reduce the section that resists bending stress

## Slide 52: Lifting & Handling

## Slide 53: Center-of-Gravity

## Slide 54: Openings in Slab Systems

## Slide 55: Center-of Gravity

## Slide 56: Questions??

## Slide 57: Hatches and Holes Design Impacts on Underground Structures
Precast Concrete Association of New York
Ronald Thornton, P.E.
Executive Director